## Data Dictionary
Column | Definition | Unit | Source | Notes / traps
Timestamp | Date and time of the measurement (YYYY-MM-DD HH:MM:SS) | datetime | All sheets | Mixed resolution: 1 sample/hour in 2020-2023, 1 sample/minute from Aug 2025
W | Instantaneous active power of the load | W (assumed) | Energy meter (BM321) | Frequently 0 when the load is off
I | Measured current | A (assumed) | Energy meter (BM321) | Often 0 when the load is off
Ea | Cumulative active energy (counter that should only increase) | kWh/Wh (assumed) | Energy meter (BM321) | Should be monotonically increasing: drops or zeros = device reset
Er | Cumulative reactive energy | kvarh/varh (assumed) | Energy meter (BM321) | Same as Ea: drops or zeros = device reset
Pa | Apparent power | VA (assumed) | Energy meter (BM321) | Normally Pa >= W
E Device type | Category of the measured load (HVAC, Lighting, Emerg. Lighting, Plugs & Sockets, Hand Dryer, RACK, Projector) | text | Metadata | Identical to the sheet name
Number of Edevices | Number of electrical devices aggregated in the row | count | Metadata | Can change over time (e.g. 73 -> 38)
Lum | Ambient light level | lux (assumed) | Environmental sensor (BSens) | 0 = missing/placeholder. Anomalous maxima: 4603 (NW), 11027 (SW)
Hum | Relative humidity | % | Environmental sensor (BSens) | 0 = missing. Real observed range approx. 20-54
Temp | Ambient temperature | °C | Environmental sensor (BSens) | 0 = missing. SW fault: up to 1411 °C
Pres | Presence flag (the only non-zero value is 1) | 0/1 | Environmental sensor (BSens) | Despite the name it does not look like pressure: it only takes 0 or 1 (hypothesis: presence/occupancy)
Notes
• Units of measure are not declared in the files: they are assumed from the type of quantity and must be confirmed with CeDInt.
• The environmental columns (Lum, Hum, Temp, Pres) are identical across all sheets of the same zone: they are zone-level data, not per-device data.
• The names "BM321" and "BSens" do not appear in the files: the grouping of columns was inferred from the task description.
• All 18 sheets share the same 12 columns in the same order.

## Missing Data
Zone | Sheet (device) | Rows | First timestamp | Last timestamp | Empty/NaN cells | % zeros Lum | % zeros Hum | % zeros Temp | % zeros Pres | % zeros Ea | % zeros W
NE | HVAC | 86719 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 100 | 100 | 100 | 100 | 0 | 25.8
NE | Plugs & Sockets | 88826 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 100 | 100 | 100 | 100 | 0 | 0.1
NW | Emerg. Lighting | 86686 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 52.5 | 11.4 | 11.4 | 84.5 | 0.1 | 0.2
NW | HVAC | 86580 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 52.5 | 11.4 | 11.4 | 84.5 | 0 | 0
NW | Hand Dryer | 88190 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 52.3 | 11.3 | 11.3 | 84.3 | 0 | 11.2
NW | Lighting | 88355 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 52.3 | 11.3 | 11.3 | 84.3 | 0 | 4.9
NW | Plugs & Sockets | 88883 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 52.4 | 11.3 | 11.3 | 84.4 | 0 | 0
NW | RACK | 86928 | 2020-04-02 23:00 | 2025-10-13 14:34 | 0 | 52.1 | 10.8 | 10.8 | 84.1 | 0 | 0
SE | Emerg. Lighting | 63970 | 2020-04-03 12:00 | 2025-10-13 14:33 | 0 | 69.3 | 1.3 | 1.3 | 79 | 3.1 | 14.7
SE | HVAC | 63958 | 2020-04-03 12:00 | 2025-10-13 14:33 | 0 | 69.3 | 1.3 | 1.3 | 79 | 3.1 | 5.8
SE | Lighting | 72551 | 2020-04-02 23:00 | 2025-10-13 14:33 | 0 | 69.4 | 5.7 | 5.7 | 81.2 | 1.8 | 50.2
SE | Plugs & Sockets | 83126 | 2020-04-02 23:00 | 2025-10-13 14:35 | 0 | 68.1 | 5.1 | 5.1 | 83 | 15 | 23.8
SE | Projector | 61689 | 2020-04-03 12:00 | 2025-10-13 14:35 | 0 | 68.6 | 1.3 | 1.3 | 78.3 | 100 | 100
SW | Emerg. Lighting | 65383 | 2020-04-03 12:00 | 2025-10-13 14:34 | 0 | 71.2 | 3.1 | 3.1 | 37.2 | 5.2 | 3.1
SW | Hand Dryer | 65894 | 2020-04-02 23:00 | 2025-10-13 14:33 | 0 | 70.8 | 3.2 | 3.2 | 36.8 | 5.4 | 18.8
SW | Lighting | 74903 | 2020-04-02 23:00 | 2025-10-13 14:34 | 0 | 71.3 | 3.4 | 3.4 | 33.8 | 3.4 | 12.6
SW | Plugs & Sockets | 69466 | 2020-04-02 23:00 | 2025-10-13 14:33 | 0 | 71.1 | 3.3 | 3.3 | 35.5 | 4.7 | 0.1
SW | RACK | 13038 | 2020-04-03 12:00 | 2021-12-03 17:00 | 0 | 52.7 | 0.2 | 0.2 | 84 | 11.9 | 0
Summary
• No empty cells or NaN, and no text in numeric fields, in any of the 18 sheets: the "holes" are hidden.
• 1) Common time gap: no data between 2023-03 and 2025-08-18 (901 days) in all sheets. Other gaps: 14 days (2022-08/09), 1 day (2022-06), etc.
• 2) Mixed resolution: hourly until 2023, per-minute from 2025; in 2025 there are also jumps of 3-5 minutes.
• 3) Zeros instead of NaN in the environmental columns: NE has 100% zeros (no usable environmental sensor); NW/SE/SW have Lum ~52-71% zeros and Pres ~34-84% zeros; Hum/Temp zeros 0-11%.
• 4) Ea/Er equal to zero: resets or missing data (SE Plugs & Sockets 15%, SW RACK 12%, SW Emerg. Lighting 5%).
• 5) SE Projector: W, I, Ea, Er, Pa are 100% zeros: dead or disconnected meter.
• 6) SW RACK: only 13,038 rows, stops at 2021-12-03 (hourly, 2022-2025 missing).
• 7) SE and SW: several sheets start on 2020-04-03 12:00 instead of 2020-04-02 23:00.
• 8) NW Emerg. Lighting: Ea is negative in 72,825 of 86,686 rows: counter not reliable.

## Anomalies
Date | Time | Sensor / Zone | What happens | Glitch type
2020-10-05 | 12:00 | NW - Plugs & Sockets | Ea = -11,646,160 (before 3,941,788, after 3,943,093); Er = 7,601,943 (expected ~2,525,000); Pa = 21,190,380 (expected ~900) | Reset with impossible spike/drop on three quantities at once
2022-04-25 | 09:00 | NW - Plugs & Sockets | Ea = 0 and Er = 0 (before 4,704,461 / 4,055,489), back to 4,710,921 at 10:00 | One-hour reset to zero
2021-07-21 | 09:00 | SE - Plugs & Sockets | Ea = 0 (before 4,223,377); 10:00 -> 940,619; 11:00 -> 1,571,709; 13:00 -> 4,228,092 | Reset with gradual recovery (three wrong values)
2025-10-08 | 18:17 | NE - Plugs & Sockets | Ea = 0, Er = 0, W = 11, I = 0; 18:20 -> 2,909,532, 18:21 -> 2,863,661, 18:22 -> 3,137,067 | Per-minute reset with unstable values after restart
2020-04-29 | 05:00 | NW - Lighting | Ea = 0, Er = 0 (before 602,343 / 577,482), then 603,914 at 06:00; W and Pa normal | Counter-only reset, power normal
2020-04-28 | 20:00 | SW - Emerg. Lighting | Ea = 0, Er = 0 at 20:00 and at 05:00 the next day, back to 82,769 at 06:00 | Reset over 2 consecutive points (with overnight gap)
2020-04-04 | 18:00 | SW - RACK | Ea = 0, Er = 0 (before 375,272 / 306,596), then 375,906 | One-hour reset to zero
2020-04-14 | 17:00 | SE - Lighting | Ea = 0, Er = 0, W = 0, I = 0, Pa = 0 for all following hours (before Ea = 8,190) | Device off or not communicating after reset
2020-04-14 | 18:00 | SW - Hand Dryer | Ea = 0, Er = 0 (before 14,559), then 24,882 at 19:00 | Reset with forward jump after recovery
2022-03-01 | 09:00 | SW - all sheets (Temp/Lum) | Temp jumps from 18.5 °C to 854 °C (up to 1,411 °C on 2022-03-02); Lum from 31 to 6,599 (11,027 at 10:00) | BSens fault/reset: lasts until 2022-03-07 09:00 (140 rows)
2025-10-05 | 16:50 | NW - all sheets (Lum) | Lum saturates at 4,603 for several consecutive minutes (16:50-16:53), then 4,504 at 16:54 and 3,071 at 16:55 | Light sensor saturation (plateau not credible)
Statistics: number of times Ea drops to 0 from a previous value above 1000: NE 29-33, NW 10-28, SE 566-4,719, SW 575-1,025 per sheet. The problem is far more frequent in SE and SW.
Note: sensor IDs are not present in the file columns; Zone + device type (sheet name) is used instead.